## Slide 1: Current and Future Activity Highlights
Mark Modera
WCEC Affiliates Forum
May 20, 2014

## Slide 2: Existing Project Highlights
Aerosol Sealing
  Multiple new contracts and proposals
  Big successes in Honda house and in New York City apartments
RTU Retrofit
  ASHRAE Standard Committee 212 launched
  First data obtained in the new climatic chamber

## Slide 3: Aerosol Envelope Sealing Honda House (Pre-Sheetrock)
Chart: ACH50
| 2009 IECC | 2012 IECC | Pre Test 1 | Post Test 1 | Pre Test 2 | Post Test 2 | Goal (Passive House)
 | 7 | 3 | 4.15 | 2.61 | 2.56 | 0.79 | 0.6

## Slide 4: Aerosol Envelope Sealing

## Slide 5: New York City Apartment Sealing
4 apartments sealed (~80%)
1-2 hours of injection (1-2 ach50)
Sound transmission measured
Fluorescence only when wet
Clear impact of humidity on process and seals

## Slide 6: Comparison of Injection and Sealing Rates
Chart: Sealing Rate [ACH50/h] OR Sealant Injection Rate [lb/h]
| NY Test 1 | NY Test 2 | NY Test 3 | Honda Test 1 | Honda Test 2
Sealing Rate | 3.4727 | 4.3521 | 2.5408 | 0.29333 | 0.3
Solid Sealant Injection Rate | 2.0364 | 2.5944 | 2.1 | 6.0624 | 1.3661

## Slide 7: Aerosol Envelope Sealing - Nozzle Testing
Characterize aerosols at different operating conditions
Determine optimal particle size and humidity for aerosol envelope sealing (and gas pipeline sealing)
Support with CFD analysis of particle drying process
P, T of compressed air
Flow of compressed air
T, RH of ambient air
Flow of ambient air
Cascade Impactor
Layflat Duct
14” Rigid Duct
Damper for pressure control

## Slide 8: Preliminary Tests

## Slide 9: RTU Retrofit - WCEC Environmental Chamber

## Slide 10: WCEC Chamber Capabilities
“Hot” Side Chamber
Temp/humidity control to wide range of climate conditions. Dehumidification for testing evaporative cooling equipment.
Airflows up to:
  5000cfm (all climate conditions)
  8000cfm (limited climate conditions)
  Airflow measurement per ASHRAE 41.2
High-accuracy chilled mirror dew-point and temperature measurements on inlet and outlet
“Cold” Side Chamber
Heating/humidification sized for cooling equipment up to 5 tons
Airflows up to 3500 cfm
Airflow measurement per ASHRAE 41.2
High-accuracy chilled mirror dew-point and temperature measurements on inlet and outlet
Can reproduce hot, dry CA climate conditions regardless of Davis weather

## Slide 11: RTU Retrofit Project
Baseline and testing of first pre-cooler in “dry” mode completed April 2014
“Wet” pre-cooler testing to follow
Baseline shows excellent agreement with AHRI

## Slide 12: Existing Project Highlights
Occupancy-Responsive Adaptive Thermostats for University Residence Halls
  SPEED Project

## Slide 13: Occupancy-Responsive Adaptive Thermostats for University Residence Halls
Improved control and facilities management
  Excellent on-board algorithms
Can achieve substantial savings (20% or more, but not always)
  Savings is sensitive to application, climate, occupancy patterns
  Thermostat needs to have full control over space to achieve savings
    Interactive effects between rooms diminish savings
    HVAC sequence of operations can essentially void control
Recommended simple tests to determine if a building will achieve savings
Simple models tend to over-predict savings

## Slide 14: Academic Period Indicated No Savings
Chart: Outdoor Air Temperature (F)
Chart: Time

## Slide 15: Non-Academic (Summer) Shows 20% Savings
Chart: Timestamp
Chart: Outdoor Air Temperature (F)

## Slide 16: Occupancy Sensing Adaptive Thermostats for University Residence Halls

## Slide 17: New Projects
Smart Power for Solar Homes
  Collaboration with UC Irvine
  HVAC solutions and battery storage to optimize peak shifting
Polymer Bead Laundry
Side by side comparison with “typical” small commercial washing machine at Capital Athletic Club
Tracer Gas Air Flow Measurement
  Commercialization funded by UCOP
  Filed provisional patent

## Slide 18: Commercialization of Tracer Gas Airflow Measurement Tools
Packaged flexible tool, software, and methods for field measurement of air flow
High accuracy: ~1.5% uncertainty up to 10,000 cfm
Large dynamic range: 50 – 50,000 cfm
Uses industrial CO2
Field Testing Generation 1.1 prototype
  Developing Generation 1.2 to cut cost by 50%

## Slide 19
Tracer Gas Airflow Measurement

## Slide 20: New Projects
Natural Gas Pipeline Sealing
  Contract in place with CEC EISG
  Pending with Scotia Gas in the UK
  Met with Fossil Fuels office at DOE
Open-Source Building Automation System
  Thermostats and RTUs
  Integration with lighting and plug load controls
  Gateway for FDD and Climate Appropriate RTUs

## Slide 21: Future Projects – Proposals in Process
Ventilation in Schools (CEC)
  CO2 and outdoor-air balancing act
Large Building Aerosol Sealing (DOD ESTCP)
  Army Corps of Engineers leakage specification
  Sub Wet-bulb Evaporative Chilling + Solar Thermal Heating (DOD ESTCP)
  RTU Solution for Energy Efficiency Using Free Cooling (DOD ESTCP)
Natural Gas Dryer Controls (CEC EISG)
  End of cycle control

## Slide 22: Future Projects – Proposals in Process
Integrated Appliances (BPA)
  Combined heating, cooling, DHW appliances
Water Chemistry (BPA/SCE)
  Water sourcing/management for evaporative cooling
  Non-chemical water treatment
  Heat-pump water heaters

## Slide 23: Future Projects – Proposals in Process
VRF plus DOAS (CEC EPIC)
  Building-level solutions
Residential HVAC Performance (CEC EPIC)
  Passive HVAC, Thermostats, FDD, Contractors
Cloud-Based Refrigeration Control (CEC EPIC)
  Collaboration with UC Davis Food Science and Industry
  Micro-Channel Absorption Chiller (CEC EPIC)
  Collaboration w/ industry

## Slide 24: Future Projects – Proposals in Process
Variable-Capacity Residential Heat Pump (CEC EPIC)
  Full-range performance testing
  System efficiency (including ducts)
Residential Thermostats (CEC EPIC)
  Low-income thermostat usability

## Slide 25: THANK YOU!
For more information, contact us at…
http://wcec.ucdavis.edu